Translated from Russian

"I CONFIRM"

First Deputy Director

- technical director of

LLC “Fergana Oil Refinery”

____  Rakhimov I.A.

________2022

TECHNICAL TASK

for design, supply, installation and commissioning works on renewal of the automated emergency protection system (ESD)

GDS installations of LLC "Fergana Oil Refinery".

FERGANA 2022

Table of contents

Customer…………………………………………………………………………………………3

Location of the design object……………………….………………………………..…………3

Name of the object…………………………………..……………………………..……………3

The basis for the renewal……………………….………………………………..……………3

Purpose of acquisition ……………………….…………………………………………………3

Source of funding ………………………….……………………………………………..…..…3

Contracting organization………………………….……………………………………………3

Staging ………………………….……………………………………………………………..…3

The name of the existing automated emergency protection systems ESD (ESDS) and the required technical characteristics………………….……….……………………….……...….3

General………………………………………………………………………………...…………4

Requirements for automated ESDS ……………………………….…………………………4

Purpose of the ESD system ……………………………………………………………....…...4

Reliability…………………………….……………………………………..………..………..…5

General requirements for the supplied ESDS equipment …………………………………6

General requirements for ESDS software…………………………………...……….………6

Requirements for the safety of information in case of accidents ……………………..……7

Standards and certification………………………..…………………………………………...7

Implementation of validation………………………………………….………………………8

Industrial safety requirements…………………………………………...…………………….8

Requirements for the method of preparation of estimates …………………………...….…8

Documentation development ……………………………………..…………………………..8

The requirement to ensure the energy efficiency of the adopted design solutions ……..8

Metrological provision…………………..…………………………………………………….8

Equipment packaging and shipping requirements …………………………………..…….8

Tagging requirements ……………………………..…………………………………………..9

Training requirements …………………………………..…………………………………..…9

Technical support requirements …………………………………………………...……….…9

Equipment supply requirement……………………………………….………………………9

STA……………………………………………….………………………………………………9

Requirements for the quality of the supplied equipment ……………………………….....9

| No. | NAME OF BASIC DATA AND REQUIREMENTS | CONTENT OF BASIC DATA AND REQUIREMENTS |
| --- | --- | --- |
| 1. | Customer | “Ferghana Oil Refinery” LLC |
| 2. | Location of the design object | 20, st. Sanoat, Fergana city, Fergana region, Republic of Uzbekistan |
| 3. | Name of the object | Installation of “Gasoil Hydrodesulfurization” |
| 4. | The basis for the renewal | Application for the purchase of inventory items for workshop No. 1 |
| 5. | Purpose of acquisition | In order to ensure trouble-free, uninterrupted and fault-tolerant operation of the ESD system of the GDS process unit of shop No. 1, troubleshoot problems associated with the ESD equipment, as well as ensure Order No. 01 dated 09.01.2009 of the head of the State Inspectorate of the Republic of Uzbekistan on supervision of safe work in industry, mining and municipal sector "SANOATKONTEKHNAZORAT" on approval of the general rules of explosion safety for fire and explosion hazardous chemical, petrochemical and oil and gas processing industries, Chapter VI. |
| 6. | Source of financing | Proprietary funds |
| 7. | Contracting organization | Determined on the basis of competitive procedures. |
| 8. | Staging | 1.Site survey and design 2.Equipment delivery 3.Installation works 4.Commissioning work 5.Commissioning into commercial operation 6.Training of operating personnel |
| 9. | The name of the existing automated AEP system (SAEP) and the required technical characteristics | Manufacturer: PAUL Hildebrandt GmbH+Co KG System: HIMA Automation System, H51-HS. Unit B5223-1. Date of manufacture: 1998. Date of commissioning: 1999г. Software: System software ELOP-I V1.0 The installation is divided into two units: HDS and SRU Separate B5223-1 unit with redundant PLC is installed for each unit. Total number of channels - 1217 of them: AI - 27 redundant DI - 492 redundant and 195 nonredundant DO - 200 redundant and 303 non-redundant. All redundant discrete input signals are integrated into “Honeywell” APCS. There are two engineering stations for message log archiving and signal monitoring. |
| 10. | General requirements for an automated AEP | - Automatic detection of potentially dangerous changes in the state of a process facility or its automation system. - Automatic measurement of technological variables important for the safe conduct of the technological process. - Automatic (on-line) diagnostics of failures occurring in the ESD system and/or in the hardware and software used by it. - Automatic actuation of ESD means that stop the development of an emergency situation (stopping pumps, compressors, conveyors, screws, opening / closing electric valves, cut-off valves, etc.) -Automatic pre-alarm signaling informing the operator of the technological process about potentially dangerous changes that have occurred in the facility or in the ESD system. - Automatic protection against unauthorized access to the settings and / or selection of the operating mode of the ESD system. - Development of procedures for controlled sequential shutdown of the technological process, machines and equipment, for which a "shock" one-time sudden stop can lead to an accident; - Continuous automatic registration of the sequence of events (SOE) affecting process safety, including potentially dangerous changes in process variables, output signals of the AEP system, personnel commands, status changes of release keys and diagnostic messages; - Ensuring high resolution in time in order to establish the exact root cause of an abnormal situation; - Automatic activation of standby technological equipment in cases specified by the plant's technological regulations. |
| 11. | Purpose of the AEP system | The ESDS should provide emergency protection functions according to the algorithms specified in the technological regulations, and be able to reconfigure when the technological process protection algorithms change. - Determination of emergencies at the technological units of the installation by interrogating sensors connected to the Sensor System in automatic mode, analyzing measured values and switching technological units to a safe state by issuing control actions on actuators in automatic mode. - Selection of reliable input information. - Analysis and logical processing of input information. - Transmission of operational information from the ESDS to the DCS for signaling, registration and archiving (parameter deviation, operation of the ESD actuators, etc.). |
| 12. | Reliability | The reliability and response time of the ESDS are determined by the developers of the ESDS, taking into account the requirements of the technological process. In this case, the category of explosion hazard of the technological blocks that make up the installation and the development time of a possible accident are taken into account. - The response time of the protection system must be guaranteed to be less than the time required for the transition of the parameter from the pre-emergency to the critical value. The reliability of security systems should be ensured by: - Hardware reservation of the required type; - Informational, functional and temporal redundancy; - Availability of systems of operational and autonomous diagnostics. The adequacy of the reservation and its type are determined and approved at a special meeting. - The installation of release keys in ESD schemes is only allowed to ensure starting, stopping or switching. The number of such keys should be minimal. At the same time, devices are provided that register all cases of disconnection of protection parameters and their duration. - The System must have hardware and software tools for diagnosing networks, stations, blocks and modules. - It must be possible to replace faulty modules in the operational mode of the ESD system. |
| 13. | General requirements for the supplied ESDS equipment | The supplier must provide a system based on the most modern technical means and the latest versions of the basic software. ESD equipment should have a modular architecture, providing for the possibility of expansion and development of APCS functions. The technical characteristics of the ESD system must correspond to the rate of change of the process parameter values within the required range. Analog input devices must provide: - input of unified current signals (4-20, 0-5) mA; - power supply of analog input circuits with voltage 24V DC; - input of signals from resistance thermometers, thermocouples. Discrete input/output devices must provide: - 24V DC power supply; - input of discrete signals 24V DC; - output of discrete signals 24V DC. Replacement of input/output modules and a reservation fully certified PLC must be carried out with the equipment running without power loss and without compromising system reliability. All external elements of the ESDS technical facilities under voltage must be protected from accidental human contact, and the technical facilities themselves must have protective grounding in accordance with the requirements of the "Electrical Installation Rules". Technical facilities must be installed in such a way as to ensure safety during their installation, adjustment, operation, maintenance and repair. Each equipment must have operational documentation (passport, form and operation manual). |
| 14. | General requirements for ESDS software | To implement the task, specialized licensed software should be used, functioning in the environment of a multitasking real-time operating system. The System software must contain a set of software modules, i.e. function blocks, which allow controlling and managing the ESDS of the installation. The system should be able to quickly configure the application software at a separate engineering station without disrupting the operability of the ESDS. All erroneous situations that occur during the operation of programs must be diagnosed, accompanied by messages, and must not cause disturbances in the operation of the ASDS. The ASDS software must meet the following requirements: Expansivity - it should be possible to make changes to the system configuration and connect additional points and contours in real time (in ON-LINE mode); Integrability - must have physical interfaces, exchange protocols for integrating information to other systems; Adaptability - compatible with a wide range of industrial computers from different manufacturers; |
| 15. | Requirements for the safety of information in case of accidents | Temporary failure of technical facilities or loss of power supply should not lead to the destruction of the accumulated or time-averaged information. The system should ensure the safety and possibility of automatic recovery of application programs and data in the following situations: - failure of technical facilities; - software failure; - power failure; - making changes to the software without stopping the system operation mode. |
| 16. | Standards and certification | The technical facilities and software of the emergency protection system must comply with the following international standards: - IEC - 61508 "Functional Safety of Electrical/Electronic/Programmable Electronic Safety-related Systems" (part 2); - IEC - 61511 "Functional safety – Safety instrumented systems for the process industry sector".(part 2); - DIN V 19250 " Control technology; fundamental safety aspects to be considered for measurment and control equipment"; - DIN V VDE 0801 "Principles for computers in safety-related systems"; - ISA-TR84.0.02 Safity Integrity level Verifications of Safity Instrumented Functions The equipment used in theESDS must be SIL2/SIL3 certified. All technical facilities (equipment) installed as part of the system must have quality certificates and a warranty period of operation. System and application software must be licensed and certified. |
| 17. | Implementation of validation | Confirmation that the proposed algorithms and project implementation fully comply with the initial requirements and technical characteristics of the existing operating system. |
| 18. | Industrial safety requirements | The development of the project must be carried out in accordance with the requirements of the current norms and rules that determine the measures for industrial safety. The ESD system must comply with the requirements of the "General rules for explosion safety for fire and explosion hazardous chemical, petrochemical and oil refining industries" and the ESDS for facilities that include technological blocks of I and II categories of explosion hazard, must be built on the basis of programmable logic controllers capable of operating according to a fail-safe structure and tested on compliance with functional safety requirements. |
| 19. | Requirements for the method preparation of estimates | Develop estimates by the resource method in current prices. |
| 20. | Documentation development | - top level project; - development of working documentation; - system assembly; - acceptance tests; - commissioning works; - combined tests. |
| 21. | The requirement to ensure the energy efficiency of the adopted design solutions | The project provides for the use of modern architectural and construction solutions, the use of energy-efficient equipment. The ESDS must have means of uninterruptible power supply, i.e. must be equipped with two independent mutually redundant power sources. |
| 22. | Metrological provision | - Equipment is subject to mandatory certification in accordance with the requirements of current legislation of the Republic of Uzbekistan and have documents permitting its use at an industrial hazardous production facility. |
| 23. | Equipment packaging and shipping requirements | Packaging and shipment must comply with all necessary requirements established by international export packaging standards to ensure the safety of the Goods during storage and transportation. Violation of the packaging may be allowed ony to check the quality, completeness, absence of damage and working characteristics of the Equipment. To ensure the safety and convenience of transportation and warehousing of equipment, the Contractor must use special packaging and packaging means adopted for this type of Equipment. |
| 24. | Tagging requirements | Equipment is subject to mandatory tagging. Tagging must be carried out in accordance with the requirements of current legislation. |
| 25. | Training requirements | Training of ESDS operating personnel shall be performed at the customer's site. The program should include training in maintenance of the hardware and software system, with the issuance of an appropriate certificate. |
| 26. | Technical support requirements | The contractor undertakes to provide technical support for 10 years. |
| 27. | Equipment supply requirement | The supply of the equipment in its entirety (or in parts) to the customer's territory must be provided by the supplier. |
| 28. | STA | The supply of equipment must include 20% of STA for all major equipment or parts whose failure could result in an incident or accident at the processing unit. |
| 29. | Requirements for the quality of the supplied equipment | All supplied equipment must be certified for compliance with the ISO9001 quality system standard for the design, development and production of software and hardware complexes for ESDS. All equipment that failed during the system assembly, acceptance tests, commissioning, combined tests, or due to incorrect selection of equipment and emergency situations not provided for in the project must be eliminated at the expense of the supplier. |

Agreed:

Chief engineer                                                    Urunbaev D.A.

Chief metrologist                                                Iminov I.R.

Members of the expert technical commission:

Head of workshop No.1                                      Shomuratov A.

Deputy head of workshop No.1                          Mirzaev I.

Head of GDS installation of w.shop No.1           Mirzaev I.

GDS installation mechanic of w.shop No.1         Matkarimov D.

Head of the ins. APCS of w.shop No.9                Almenov I.N.

Senior foreman of workshop No.9                       Lutfullaev Sh.Sh.