Translated from Russian

DATA SHEET FOR THE CONTROL CABINET OF THE APCS OTU SHIRKENT

| No. in order | Requested data | Unit of measure | Specifications, data |
| --- | --- | --- | --- |
| 1 | Purpose of equipment | - | Control of process parameters of OTU, control and management of OTU equipment |
| 2 | Equipment identification note | 3 | PLC cabinet |
| 3 | Location of equipment | 3 | OTU of the Shirkent field |
| 4 | Explosion and fire hazard zone class | - | no |
| 5 | Category and group of explosive mixture | - | no |
| 6 | Climatic modification. State industry standard 15150-69 | - | NF 4 |
| 7 | Environment temperature | °C | From -20 to +90 |
| 8 | Degree of protection against moisture and dust according to State industry standard 14254-2015, not lower than | - | IP 43 |
| 9 | Dimensional specifications (without base). HxWxD, max | mm | 1200 x 600 x 400 (can be scaled up to standard ground version if required) |
|  | Cabinet version | - | Ground type |
| 10 | Door version | - | Single winged |
|  | Coating quality in terms of appearance, not worse | - | Class IV according to State industry standard 9.032-74 |
| 11 | Cable entry | - | Bottom in floor version |
| 12 | Power supply voltage | V | Single-phase, - 220 V, 50 Hz |
| 13 | Amount of power input from Control station boards | pcs | 1 (per cabinet) |
| 14 | Amount of power input from external UPS | pcs | 2 (per cabinet) |
| 15 | Power consumption, max | VA | 1500 |
| 16 | Erected grounding system for cabinet elements | - | Yes |
| 17 | Internal grounding bar of the cabinet | - | Yes |
|  |  |  | (See note 3, 4) |
| 18 | Supplying external devices with DC voltage | - | Yes |
| 19 | Uninterruptible power supply | VA | 1500 |
| 20 | CC: |  |  |
|  | Type of equipment | - | CPU modules |
|  |  |  | REGUL RX00 series PLC |
|  | Chassis | pcs | (See note 6) |
|  | CC main with ports | pcs | (See note 6) |
|  | Ethernet and hot standby support |  |  |
|  | Ethernet modules of the main CC | pcs | (See note 6) |
|  | Communication modules of the LPK network of the main CC |  | (See note 6,7) |
|  | CC standby with ports | pcs | (See note 6) |
|  | Ethernet and hot standby support |  |  |
|  | Standby CC Ethernet Modules | pcs | (See note 6) |
|  | Communication modules of the PLC network of the standby CC | pcs | (See note 6,7) |
|  | Power modules | pcs | 1 per chassis |
| 21 | PLC (Power Line Communication) |  |  |
|  | Type of equipment | - | REGUL RX00 series PLC modules |
|  | Chassis | pcs | (See note 6) |
|  | PLC network communication modules | pcs | Yes |
|  |  |  | (See note 6,7) |
|  | PLC Network Communication Module Ports | pcs | Yes |
|  |  |  | (See note 6,7) |
|  | Power module | pcs | Yes |
|  |  |  | (See note 6) |
|  | Input/output module | pcs | Yes |
|  |  |  | (See note 6) |
|  | RS-485 modules | pcs | Yes |
|  |  |  | (See note 6) |
| 22 | Analog input | - | Yes |
|  |  |  | (See note 6,9) |
| 23 | Input analog signals 4-20 mA | pcs | 64 (See note 6, 12, 21) |
| 24 | Analog output | - | Yes |
|  |  |  | 9 (See note 8,9) |
| 25 | Output analog signals 4-20 mA | pcs | (See note 8, 12, 21) |
| 26 | Discrete inputs | - | Yes |
|  |  |  | (See note 10) |
| 27 | Input discrete signals -24 V | pcs | 4 (See note 6,12, 21) |
| 28 | Input discrete signals -220 V | pcs | (See note 6,12, 21) |
| 29 | Discrete outputs | pcs | Yes |
|  |  |  | (See note 11) |
| 30 | Output discrete signals - 24 V | pcs | 10 (See note 6,12, 21) |
| 31 | Output discrete signals - 220 V | pcs | (See note 6,12, 21) |
| 32 | Total analog input signals | pcs | (See note 6,12) |
| 33 | Total analog output signals | pcs | (See note 6,12) |
| 34 | Total discrete input signals | pcs | (See note 6, 10, 12) |
| 35 | Total discrete output signals | pcs | (See note 6, 11, 12) |
| 36 | RS-485 interface |  | 1 (See note 6,12) |
|  | Workstation Operator Equipment |  |  |
| 37 | Workstation operator with pre-installed basic and specialized software (including the development of application controller software and commissioning), licenses (SCADA, MS Office, Antivirus) | pcs | 1 |
| 38 | Possibility to connect WEB client | pcs | Yes |
| 39 | Monitor 27" | pcs | 2 |
| 40 | Engineering station (laptop) with pre-installed basic and specialized software, licenses (PCC development environments, SCADA, MS Office. Antivirus) | pcs | 1 |
| 41 | Uninterruptible power supply for Workstation | pcs | Yes, battery life 60 min, with diagnostic connection board |
| 42 | Report printer | pcs | 1 |
| 43 | Communication equipment for connection Workstation | pcs | FX - TX |
| 44 | Communication equipment: | pcs |  |
|  | Top-level network switch | pcs | 1 |
|  |  |  | Managed L2 switch |
|  | Number of ports / LAN type / connector type | pcs | 8/Ethernet 10/100 BASE-T/ |
|  |  |  | RJ-45 |
|  | Transfer mode | pcs | 10 Half / Full Duplex |
|  |  |  | 100 Full Duplex |
|  | Automatic transmission speed matching and MDI/MDIX auto detection | - | Yes |
|  | Optical port based on removable transceiver / number / port connector type | - | no |
|  | Type of optical fiber connection | - | no |
|  | Supported standards | - | IEEE802,1P |
|  |  |  | JEEE 802.10 for VLANs |
|  |  |  | IEEE802.1V for RSTP |
|  |  |  | IEEE 802.3 for 10BaseT |
|  |  |  | IEEE 802.3u for 100BaseT(X) |
|  | Supported protocols | - | NTP (SNTP), SNMP(v3), HTTPS, SSH |
|  | Monitoring by SNMP(v3) | - | Yes |
|  | Broadcast traffic restriction function | - | Yes |
|  | Console cable for switch configuration | pcs | 1 |
| 45 | Gateway or switch or PLC network media converter | pcs | no |
| 46 | Installation version of communication equipment | - | Mounting on a DIN rail |
| 47 | Power supply communication equipment | - | From 2 inputs through uninterruptible power supplies, reserved according to the diode "ИЛИ" scheme |
|  |  |  | Supply voltage - 24 V ±20% DC from cabinet |
| 48 | Additional equipment mounted in the cabinet: |  |  |
| 49 | Availability of Class III surge protection device | set | Yes |
| 50 | A set of devices for organizing power inside the cabinet, including secondary power supplies -220/=24V with rechargeable batteries for powering baskets, gateways of switches / media converters, etc. | set | Yes |
| 51 | Cabinet lighting | - | Yes |
|  |  |  | (See note 16) |
| 52 | Service socket, min | pcs | 1 |
| 53 | Temperature sensor for monitoring the temperature inside the cabinet with a 4-20mA output signal and 2-wire connection for monitoring the temperature inside the cabinet | pcs | 1 |
| 54 | Cabinet door opener signaling device |  | 2 |
| 54 | Clip connectors | - | For connecting cables with a core cross |
|  |  |  | section of up to 2.5 mm² |
| 55 | Intrinsically safe barriers for analogue sensors | pcs | Yes, according to the number of instrumentation and automation |
| 56 | Set of terminating resistors for RS485 interface lines (R=120 OM) | set | Yes, by the number of connected RS485 lines |
| 57 | Fastener elements | set | 1 |
| 58 | Filing Pocket on the cabinet door | pcs | 1 |
| 59 | Availability of design (working) documentation in accordance with GOST (state industry standard) 34 201 89 | set | Yes |
| 60 | Availability of Passport (form) | - | Yes |
| 61 | Availability of instructions (manual) for use | - | Yes |
| 62 | Availability of a certificate of compliance with the requirements of TR CU "On the safety of equipment for operation in explosive environments" (TR CU 012/2011) | - | Yes, for Ex components |
| 63 | Availability of an expert opinion on compliance with industrial safety requirements, included in the register of Rostekhnadzor (Federal Service for Ecological, Technological and Nuclear Supervision), or a certificate of compliance with the requirements of TR CU 012/2011 | - | Yes |
| 64 | Availability of a certificate of type approval of the measuring system (IS), a description of the type of IS (an appendix to the certificate of approval of the type of IS) and a methodology for certifying IS (copies) regulated in the annex (description of the type of IS) to this certificate |  | Yes |
| 65 | Conformity | - | - |
| 66 | Software | - | Yes |
| 67 | Installation supervision | - | Yes |
| 68 | Commissioning | - | Yes |

Notes:

1. The quick-release panel (if any) must be secured to the cabinet with quick-release devices with locks identical to the front door of the cabinet, locking tabs (opening the front door and back panel must be done with one key).

2. Implementation of the power supply circuit inside the programmable logic controller (ПЛК) cabinet is determined by the manufacturer of the Automated Process Control System (АСУТП).

3. An internal grounding bar must be installed inside the cabinet. On the internal ground bus of the cabinet there must be a bolted connection of at least 6 mm* section conductor for connection to the grounding bar of the room automation equipment. Measures against loosening and corrosion of the contact connection must be provided for the bolted connection.

4. A grounding bar must be provided for grounding the metal parts of the cabinet enclosure, cable armor, and cabinet equipment at the bottom. The grounding bus must be made in the horizontal plane. Grounding bolts and nuts shall be M6 (5) threaded. The number of bolts must be at least half + 20% reserve of grounding conductors, assuming that more than two grounding conductors will be connected to one bolt. Three washers each must be installed on the bolts.

5. Specialized ground connectors must be provided inside the enclosure to connect loose cable conductors, PE conductors in cables, and cable shields. Specialized connectors must be supplied in sufficient volume to ground all unused conductors of cables, PE conductors and cable shields and, if necessary, mounted during commissioning work (ПНР). Specialized ground connectors must be mounted on the DIN rail on which the terminal connectors of the cable to be connected are mounted. Specialized ground connectors must ensure a guaranteed electrical contact with the metal parts of the cabinet (DIN rail). The DIN rail on which the specialized ground connectors are mounted must be connected to the internal grounding bar of the cabinet with a 6 sq.mm conductor.

6. Type of REGUL RXOD series controller equipment and its quantity is determined by the supplier-manufacturer of the APCS (АСУТП) depending on the information volume.

7. Interfaces and protocols for data transmission inside the PLC cabinet (PLC network), the topology for connecting the input/output chassis (star, bus) to gateways or switches must be made in accordance with the technical characteristics of the REGUL RX00 series controller equipment.

8. The resulting error of the measuring channel should not exceed 15% of the error included in this measuring channel of the primary measuring transducer. The measuring channel includes a primary measuring transducer (sensor), a communication line, a normalizing transducer (if any), an analog signal input module, including the conversion algorithms used in these devices. The analog input modules must be selected with the above requirement in mind.

9. When using sensors with 4-20mA+HART interface, HART protocol is used only for sensor configuration and diagnostics. The cabinet must be able to connect a portable HART terminal to set up and configure the sensor parameters.

10. The number of discrete signals is given without cabinet service signals. The list and number of service signals must be determined by the supplier-manufacturer of APCS in accordance with the hardware implementation of the cabinet.

11. All output channels of the external alarm activation, power supply to the alarm channels and the "STOP" command of executive mechanisms (valves of auxiliary system units) must be protected by fuses with visual status control except in cases for which the wiring diagrams do not show fuses for the "STOP" command of executive mechanisms.

12. The PLC cabinet must have a reserve for interface ports, for input and output channels of each type, at least 15% - with output to terminal connectors, an additional 5% - for terminal blocks.

13. Power supply of mutually reserve instrumentation must be carried out from reserve 220/24V converters through their own circuits and lithium-ion batteries.

14. Provide reserve power supply for equipment powered by -220V inside the cabinet.

15. The cabinet must be provided with lighting and equipped with a 220V AC socket. Sockets and lighting must be connected to 220V AC mains from an input that is not connected to an uninterruptible power supply (if any) through separate circuit breakers. Lighting should be switched on when the cabinet doors are opened. Manual lighting switches must be provided in the automation cabinets.

16. The supplier-manufacturer of the APCS must provide circuit breakers, fuses, light signaling, intermediate relays, etc. in the cabinet. in a volume that ensures the safe operation of the PLC cabinet as part of the APCS.

17. Devices and elements that are part of the PLC cabinet and located in the input-output, power and data circuits must be protected from induction of an additional (spurious) signal, impulse noise, overvoltage and secondary effects of lightning.

18. PLC electrical cabinet diagrams (including power supply diagrams) must be developed by the supplier-manufacturer of the process control system on the basis of this DS, structural diagram, list of terminal fields of the PLC cabinet and agreed with the Customer.

18 All documentation must be done in Russian.

19. The characteristics of the operator's WKS, engineering station, as well as the list of software should be agreed with the customer.

21. The list of signals is mandatory for this DS.

Chief Engineer of TTP Karshi      Grebenev A.V.

Head of OAandM TTP Karshi      Khimmatov F.T.

List of APCS and MOC signals for the project "Reconstruction of OTU Shirkent”.

| Control | Signaling | Regulation | Measurement | APCS cabinet Type and kind of signals |  |  |  |  |  | Equipment on site | Measurement range | Position |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | On site | RS-485 | DO | DI | AO | Al |  |  |  |
|  | X |  | X |  |  |  |  |  | 4 | Pressure indicator (high, low pressure and measured) | 4-20mA, range 0-6MPa | Inlet manifolds |
|  | X |  | X |  |  |  |  |  | 2 | Temperature indicator (high, low pressure and measured) | 4-20mA, range 0-100C |  |
|  |  |  |  | 8 |  |  |  |  |  | Manometer | Range 0-6MPa |  |
|  | X | ---------- | X |  |  |  |  |  | 1 | Equalizer | 4-20mA, measurement range 0-1900 mm | C-1 |
|  | X |  | X |  |  |  |  | 1 | 1 | Level control valve | DN-100, SWG-2.5MPa. |  |
|  | X |  | X |  |  |  |  |  | 1 | Pressure indicator | 4-20mA, range 0-2,5MPa |  |
|  | X |  | X |  |  |  |  | 1 | 1 | Pressure control valve | DN-100, SWG-6MPa. |  |
|  |  |  |  | 2 |  |  |  |  |  | Manometer | Range 0-2,5MPa |  |
|  |  |  |  |  |  |  |  |  |  | Manometric thermometer | Range 0-100C |  |
|  | X | --------- | X |  |  |  |  |  | 1 | Equalizer | 4-20mA, measurement range 0-1100 mm | C-2 |
|  | X |  | X |  |  |  |  | 1 | 1 | Level control valve | DN-100, SWG-2.5MPa, Q-250-500m3/day |  |
|  | X |  | X |  |  |  |  |  | 1 | Pressure indicator | 4-20mA, range 0-2,5MPa |  |
|  | X |  | X |  |  |  |  | 1 | 1 | Pressure control valve | DN-100, SWG-2.5MPa, Q-50000-75000m3/day |  |
|  |  |  |  | 2 |  |  |  |  |  | Manometer | Range 0-2,5MPa |  |
|  |  |  |  |  |  |  |  |  |  | Manometric thermometer | Range 0-100C |  |
|  | X | ----------- | X |  |  |  |  |  | 1 | Equalizer | 4-20mA, measurement range 0-600 mm | C-3 |
|  |  |  |  |  |  |  |  | 0 | 0 | Level control valve | DN-100, SWG-2.5MPa, Q-250-500m3/day |  |
|  | X |  | X |  |  |  |  |  | 1 | Pressure indicator | 4-20mA, range 0-2,5MPa |  |
|  |  |  |  | 2 |  |  |  |  |  | Manometer | Range 0-2,5MPa |  |
|  | X | ----------- | X |  |  |  |  |  | 1 | Equalizer | 4-20mA, measurement range 0-2995 mm | O-1 |
|  | X |  | X |  |  |  |  | 1 | 1 | Level control valve | DN-100, SWG-2.5MPa, Q-250-500m3/day |  |
|  | X |  | X |  |  |  |  |  | 2 | Pressure indicator | 4-20mA, range 0-2,5MPa |  |
|  |  |  |  |  |  |  |  | 0 | 0 | Pressure control valve | DN-100, SWG-2.5MPa, Q-50000-75000m3/day |  |
|  |  |  |  | 2 |  |  |  |  |  | Manometer | Range 0-2,5MPa |  |
|  | X |  | X |  |  |  |  |  | 3 | Temperature indicator | 4-20mA, measurement range 0-100C |  |
|  | X |  | X |  |  |  |  |  | 1 | Equalizer | 4-20mA, measurement range 0-1900 mm | E-1 |
|  | X |  | X |  |  |  |  |  | 1 | Pressure indicator | 4-20mA, range 0-2,5MPa |  |
|  |  |  |  | 2 |  |  |  |  |  | Manometer | Range 0-2,5MPa |  |
|  | X |  | X |  |  |  |  |  | 1 | Equalizer | 4-20mA, measurement range 0-1900 mm | E-6 |
|  | X |  | X |  |  |  |  |  | 1 | Pressure indicator | 4-20mA, range 0-2,5MPa |  |
|  |  |  |  | 2 |  |  |  |  |  | Manometer | Range 0-2,5MPa |  |
|  |  |  |  |  |  |  |  |  | 1 | Equalizer | 4-20mA, measurement range 0-8800 mm | E-7 |
|  | X |  | X |  |  |  |  |  | 1 | Pressure indicator | 4-20mA, range 0-2,5MPa |  |
|  |  |  |  |  |  |  |  |  |  | Manometer | Range 0-2,5MPa |  |
|  | X |  | X |  |  |  |  |  | 1 | Equalizer | 4-20mA, measurement range 0-2900 mm | E-8 |
|  | X |  | X |  |  |  |  |  | 1 | Pressure indicator | 4-20mA, range 0-2,5MPa |  |
|  |  |  |  |  |  |  |  |  |  | Manometer | Range 0-2,5MPa |  |
|  | X |  | X |  |  |  |  |  | 1 | Equalizer | 4-20mA, measurement range 0-3200 mm | E-9 |
|  | X |  | X |  |  |  |  |  | 1 | Pressure indicator | 4-20mA, range 0-2,5MPa |  |
|  |  |  |  | 2 |  |  |  |  |  | Manometer | Range 0-1,6MPa |  |
|  |  |  |  |  | 1 |  |  |  | 2 | Flame control indicator | Brand SL-01 | PP-0.63 A/B |
|  | X |  | X |  |  |  |  |  | 4 | Inlet and outlet pressure indicator | Ethernet RS-485, range 0-2,5 MPa |  |
|  | X |  | X |  |  |  |  |  | 8 | Temperature indicator ((inlet, outlet, smoke, heat exchanger) | Ethernet RS-485, range 0-150C |  |
|  | X |  | X |  |  |  | 2 |  |  | Level indicator | Float brand DRU-1 |  |
|  |  |  |  |  |  |  |  | 0 | 0 | Gas metering unit | RS-485 flow from 0-50 m3/h |  |
|  |  |  |  | 4 |  |  |  |  |  | Manometer | Range 0-2,5MPa |  |
|  |  |  |  |  |  |  | 1 |  |  | ECM at the inlet of FHF | Range 0-1,6MPa |  |
|  |  |  |  |  |  |  | 1 |  |  | ECM at the outlet of FHF | Range 0-0,5MPa |  |
|  |  |  |  |  |  | 3 |  |  |  | Solenoid valve of FHF | Power supply 24V |  |
|  |  |  |  |  |  | 3 |  |  |  | Manometric thermometer | Range 0-100C |  |
|  | X |  | X |  |  | 2 |  |  | 2 | Equalizer | 4-20mA, measurement range 0-1000 mm | Pumping PDT A/B |
|  |  |  |  |  |  |  |  |  | 1 | Liquid metering unit | SWG-2.5MPa, DN-168mm, Q-250t/day |  |
|  |  |  |  | 2 |  |  |  |  |  | Manometer | Range 0-2,5MPa |  |
|  | X |  | X |  |  | 2 |  |  | 2 | Pressure indicator | 4-20mA, range 0-2,5MPa | Pumping CRL A/B |
|  |  |  |  | 2 |  |  |  |  |  | Manometer | Range 0-2,5MPa |  |
|  | X | ------- | X |  |  |  |  |  | 1 | Equalizer | 4-20mA, measurement range 0-1900 mm | Long term operation |
|  | X |  | X |  |  |  |  | 1 | 1 | Level control valve | DN-100, SWG-2.5MPa |  |
|  | X |  | X |  |  |  |  |  | 1 | Pressure control | 4-20mA, range 0-2,5MPa |  |
|  | X |  | X |  |  |  |  | 1 | 1 | Pressure control valve | DN-100, SWG-6MPa |  |
|  |  |  |  | 1 |  |  |  |  |  | Manometer | Range 0-2,5MPa |  |
|  |  |  |  |  |  |  |  |  |  | Manometric thermometer | Range 0-100C |  |
|  | X | -------- | X |  |  |  |  |  | 1 | Equalizer | 4-20mA, measurement range 0-1900 mm |  |
|  | X |  | X |  |  |  |  | 1 | 1 | Level control valve | DN-100, SWG-2,5MPa |  |
|  | X |  | X |  |  |  |  |  | 1 | Pressure control | 4-20mA, range 0-2,5MPa |  |
|  | X |  | X |  |  |  |  | 1 | 1 | Pressure control valve | DN-100, SWG-6MPa |  |
|  |  |  |  | 1 |  |  |  |  |  | Manometer | Range 0-2,5MPa |  |
|  |  |  |  |  |  |  |  |  |  | Manometric thermometer | Range 0-100C |  |
|  |  |  |  |  |  |  |  |  | 1 | Equalizer | 4-20mA, measurement range 0-1900 mm |  |
|  |  |  |  |  |  |  |  |  | 1 | Pressure control | 4-20mA, range 0-2,5MPa |  |
|  |  |  |  | 1 |  |  |  |  |  | Manometer | Range 0-2,5MPa |  |
|  |  |  |  |  |  |  |  |  | 1 | Equalizer | 4-20mA, measurement range 0-1900 mm |  |
|  |  |  |  |  |  |  |  |  | 1 | Pressure control | 4-20mA, range 0-2,5MPa |  |
|  |  |  |  | 1 |  |  |  |  |  | Manometer | Range 0-2,5MPa |  |

Chief Engineer of TTP Karshi      Grebenev A.V.

Head of OAandM TTP Karshi      Khimmatov F.T.